## Al Majd North SLFP last
ASSET_TAG | Maximo Asset Number | Latitude | Longtitude | KM_ELECTRICITY_NUMBER | KM_CABINET_EARTHPIT_AVAILABILITY | SLFP_LEVEL_VS_FFL ASPHALT | WAYS_OUTPUT | NO_OF_SPARE_AVAILABILITY | SLFP CONDITION | MCCB_CAPACITY | KM MCCB (A) | METERED | INCOMING_SUPPLY (V) | SLFP_THIRD_PARTY_CONNECTION | SLFP_THRID_PARTY_DETAIL | CABLE_SIZE | SS & FEEDER NO. | CONTACTOR | FP_MAIN_BREAKER_SIZE | CONTACTOR_CAPACITY | CT_AVAILABILITY | Inrush_RED | Inrush_YELLO | Inrush_BLUE | Inrush Currunt % | Running_RED | Running_YELLO | Running_BLUE | Running Currunt % | DESCRIPTION | REMARKS | OTHER REMARKS | DEALY_TIMER & SECONDARY_ CONTACTOR_AVAILABILITY | EARTHING | EARTHING_PIT_CONDITION | EARTHING_RESISTANCE_VALUE (OHM) | DRAWING_POCKET | DRAWING_INSIDE POCKET | DOOR_LOCK_CONDITION | DOOR_AVAILABILITY | DOOR_CONDITION | GASKET_CONDITION
P3-5C | 13159559 | 25.4865 | 51.3439 | 1283463 | No | Higher than asphalt level | 8 | 9 | Not Good | 200 | 100 | Yes | 416 | N/A | No | 70 | 25800/F4 | Yes | 200 | 200 | Yes | 81 | 76 | 52 | 70% | 37 | 37 | 24 | 33% | Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | All good Re-Survey 14 April 2026 | No | Yes | Good | 0.41 | Yes | Yes | Good | Yes | Good | Good
P3-TU-1 | 13160084 | 25.4831 | 51.3425 | 1283461 | No | Higher than asphalt level | 8 | 10 | Not Good | 100 | 100 | Yes | 431 | N/A | N/A | 70 | 25800/F1 | Yes | 200 | 250 | Yes | 50 | 34 | 44 | 43% | 17 | 15 | 17 | 16% | Corroded/Rusted, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification, Others | Around the Earth pit and foundation back filling is bad Re-Survey 16 April 2026 | No | Yes | Very Poor | 0.87 | Yes | Yes | Good | Yes | Good | Good
P3-TU-3 | 13160086 | 25.4817 | 51.3435 | 1283459 | Yes | Higher than asphalt level | 8 | 10 | Normal | 200 | 100 | Yes | 416 | N/A | N/A | 70 | 25800/F2 | Yes | 200 | 250 | Yes | 27 | 26 | 17 | 24% | 11 | 9 | 10 | 10% | Corroded/Rusted, Others | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition is ok, Re-Survey 15 April 2026 | No | Yes | Good | 0.8 | Yes | Yes | Good | Yes | Good | Good
P3-5 |  | 25.4817 | 51.3436 | 1273304 | No | Higher than asphalt level | 8 | 6 | Not Good | 100 | 100 | Yes | 416 | N/A | N/A | 70 | 25800/F3 | Yes | 200 | 250 | Yes | 132 | 108 | 89 | 110% | 79 | 64 | 61 | 68% | Corroded/Rusted, Fadded paint or tagging, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Others | All door hinge are broken and over all condition is ok, Re-Survey 15 April 2026 | No | Yes | Good | 0.65 | Yes | No | Very Poor | Yes | Very Poor | Very Poor
P3-4 | 13160088 | 25.4782 | 51.3421 | 1273303 | No | Higher than asphalt level | 8 | 10 | Not Good | 200 | 100 | Yes | 422 | N/A | N/A | 70 | 25799/F2 | Yes | 200 | 250 | Yes | 60 | 27 | 96 | 61% | 75 | 68 | 58 | 67% | Corroded/Rusted, Fadded paint or tagging, Foundation backfilled | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification, Others | In panel light missed, Over all condition is ok, Re-Survey 16 April 2026 | No | Yes | Good | 0.77 | Yes | Yes | Good | Yes | Good | Average
P3-3 | 13160090 | 25.4735 | 51.3419 | 1273302 | No | Higher than asphalt level | 8 | 6 | Not Good | 100 | 100 | Yes | 416 | N/A | N/A | 70 | 25799/F1 | Yes | 200 | 200 | Yes | 87 | 92 | 66 | 82% | 55 | 55 | 46 | 52% | Others | Others | All avag, Re-Survey April 16 2026 | Yes | Yes | Good | 1.46 | Yes | Yes | Good | Yes | Good | Average
P1-12 | 13151083 | 25.5219 | 51.3454 | 1274712 | No | Higher than asphalt level | 6 | 0 | Bad | 200 | 100 | Yes | 416 | N/A | NA | 70 | No SS Number | Yes | 200 | 200 | No | 110 | 113 | 81 | 101% | 107 | 104 | 92 | 101% | Corroded/Rusted, Fadded paint or tagging, Foundation backfilled, Panel location in low level area, Panel damaged and replaced, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification, Found pole foundation burried/ backfilled, Found expossed cable, Found damage foundation, Found unused cable inside the feeder pillar panel, Found water accumulation/ stagnant water in the surrounding, Panel has been newly replaced due to aging and deterioration, Panel has been newly replaced due to accidental damage, Others | Very poor , Re-Survey 15-April-2026 | No | No | N/A | 0 | No | N/A | Average | Yes | Average | Average
P1-11 |  | 25.5152 | 51.3449 | 1274713 | No | Higher than asphalt level | 8 | 6 | Not Good | 200 | 150 | Yes | 423 | N/A | N/A | 70 | 25802/F2 | Yes | 200 | 250 | Yes | 120 | 119 | 127 | 122% | 70 | 67 | 69 | 69% | Corroded/Rusted, Fadded paint or tagging | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification, Others | 2 door hinge are broken and over all condition is ok, Re-Survey 15-April-2026 | No | Yes | Good | 1.24 | Yes | Yes | Average | Yes | Very Poor | Average
P1-10 | 13151085 | 25.5096 | 51.3445 | 1274733 | No | Higher than asphalt level | 8 | 6 | Not Good | 200 | 150 | Yes | 421 | N/A | N/A | 70 | 25802/F1 | Yes | 200 | 200 | Yes | 89 | 97 | 91 | 92% | 93 | 90 | 81 | 88% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition is ok, Re-survey 15 April 2026 | No | Yes | Good | 1.51 | Yes | Yes | Good | Yes | Good | Good
P1-9 | 13151086 | 25.5026 | 51.3439 | 1274761 | Yes | Higher than asphalt level | 8 | 6 | Not Good | 200 | 150 | Yes | 417 | N/A | N/A | 70 | 25801/F2 | Yes | 200 | 250 | Yes | 149 | 93 | 108 | 117% | 94 | 77 | 80 | 84% | Corroded/Rusted, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Others | 2 door hinge are broken and over all condition is ok, Re-Survey 15-April-2026 | No | Yes | Good | 1.18 | Yes | Yes | Average | Yes | Very Poor | Average
P3-6 | 13159554 | 25.4969 | 51.3435 | 1273259 | No | Higher than asphalt level | 8 | 3 |  | 200 | 150 | Yes | 416 | N/A | No | 70 | 25810/F1 | Yes | 200 | 250 | Yes | 134 | 157 | 156 | 149% | 119 | 84 | 103 | 102% | Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Feeder pilar inside breaker channel no good.also kharamaa cabinet main cable insulation fully damage. Need to maintence. Re-Survey 15 April 2026 | No | Yes | Good | 1.15 | Yes | Yes | Average | Yes | Good | Average
P3-TU-2 | 13159555 | 25.4883 | 51.3429 | 1283460 | No | Higher than asphalt level | 8 | 8 | Normal | 200 | 200 | Yes | 416 | Yes | Terannel lights | 70 | 25792/F5 | Yes | 200 | 200 | Yes | 49 | 28 | 25 | 34% | 6 | 11 | 12 | 10% | Others | Others | All ok, Re-Survey 15 April 2026 | No | Yes | Average | 0.53 | Yes | Yes | Good | Yes | Good | Good
P3-5F | 13159555 | 25.4882 | 51.3429 | 1273307 | No | Higher than asphalt level | 8 | 6 | Not Good | 200 | 150 | Yes | 416 | N/A | No | 70 | 25800/F2 | Yes | 200 | 250 | Yes | 132 | 141 | 177 | 150% | 114 | 110 | 118 | 114% | Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Feeder pilar inside breaker channel no good. Need to maintence. Re-Survey 14 April 2026 | No | Yes | Good | 0.36 | Yes | Yes | Average | Yes | Average | Average
P3-TU-4 | 13159558 | 25.4866 | 51.3438 | 1283458 | No | Higher than asphalt level | 8 | 10 | Not Good | 200 | 150 | Yes | 416 | Yes | Terennl lighting | 70 | 25800/F4 | Yes | 200 | 200 | Yes | 25 | 17 | 21 | 21% | 11 | 8 | 9 | 9% | Others | Others | All good Re-Survey 15 April 2026 | No | Yes | Good | O.41 | Yes | Yes | Good | Yes | Good | Good
P1-21 | 13160117 | 25.5778 | 51.3494 | 1274773 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 200 | Yes | 424 | N/A | N/A | 70 | 25808/F2 | Yes | 200 | 250 | Yes | 79 | 88 | 58 | 75% | 76 | 65 | 54 | 65% | Corroded/Rusted, Panel damaged and replaced, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Others | Door is damage, Re-Survey 14 April 2026 | No | Yes | Average | 0.75 | Yes | Yes | Good | Yes | Very Poor | Poor
P1-20 | 13160118 | 25.5723 | 51.349 | 1274778 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 416 | N/A | No | 70 | 25808/F1 | Yes | 200 | 250 | Yes | 70 | 31 | 75 | 59% | 85 | 81 | 77 | 81% | Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Inrush current too much.Some breaker have off position. Need to check. Re-Survey 14 April 2026 | No | Yes | Good | 0.77 | Yes | Yes | Average | Yes | Average | Average
P1-19 | 13160119 | 25.5651 | 51.3485 | 1274714 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 200 | Yes | 416 | N/A | N A | 70 | 25807/F2 | Yes | 200 | 250 | Yes | 74 | 115 | 64 | 84% | 72 | 68 | 75 | 71% | Foundation backfilled, Others | Others | In side wiring not poor lode not blanchad, Re-Survey 14 April 2026 | No | Yes | Average | 1.46 | Yes | Yes | Good | Yes | Good | Good
P1-18 | 13160120 | 25.5597 | 51.3481 | 1277114 | No | Higher than asphalt level | 8 | 6 | Not Good | 200 | 200 | Yes | 416 | N/A | No | 70 | 25807/F1 | Yes | 200 | 250 | Yes | 123 | 117 | 138 | 126% | 65 | 79 | 81 | 75% | Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Kharamaa meter cabinet door damage. Also ampere need balance. Re-Survey 14 April 2026 | No | Yes | Average | 1.83 | Yes | Yes | Average | Yes | Average | Average
P1-17 |  | 25.5526 | 51.3476 | 1277118 | Yes | Higher than asphalt level | 8 | 6 | Normal | 200 | 200 | Yes | 416 | N/A | N A | 70 | 25806/F2 | Yes | 200 | 200 | Yes | 128 | 123 | 128 | 126% | 68 | 71 | 66 | 68% | Others | Others | NOTE # kharama incomer power supply cable insulation fully damaged condition, need to rectify. Km door also missing, Re-Survey 14 April 2026 | No | Yes | Good | 2.36 | Yes | Yes | Good | Yes | Good | Good
P1-16 | 13160122 | 25.5471 | 51.3472 | 1276381 | No | Higher than asphalt level | 8 | 3 | Not Good | 200 | 200 | Yes | 425 | N/A | N/A | 70 | 25806/F1 | Yes | 200 | 250 | Yes | 126 | 123 | 141 | 130% | 64 | 55 | 75 | 65% | Corroded/Rusted, Fadded paint or tagging | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition is ok, Re-Survey 14 April 2026 | No | Yes | Good | 1.05 | Yes | Yes | Good | Yes | Good | Good
P1-15 |  | 25.54 | 51.3467 | 1276378 | No | Higher than asphalt level | 8 | 6 | Not Good | 200 | 200 | Yes | 427 | N/A | N/A | 70 | 25804/F2 | Yes | 200 | 250 | Yes | 92 | 110 | 104 | 102% | 50 | 59 | 57 | 55% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition is ok, Re-Survey 14 April 2026 | No | Yes | Good | 0.6 | Yes | Yes | Good | Yes | Good | Good
P1-14 | 13151081 | 25.5345 | 51.3462 | 1277115 | Yes | Higher than asphalt level | 8 | 6 | No | 200 | 200 | Yes | 421 | N/A | N/A | 70 | 25804/F1 | Yes | 200 | 250 | Yes | 50 | 52 | 121 | 74% | 86 | 82 | 83 | 84% | Corroded/Rusted, Fadded paint or tagging | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification | Over all condition is ok, Re-Sruvey 15 april 2026 | No | Yes | Good | 0.48 | Yes | Yes | Good | Yes | Good | Good
P2-18 | 13159545 | 25.6166 | 51.3667 | 1276377 | No | Higher than asphalt level | 8 | 6 | Balanced | 200 | 200 | Yes | 416 | N/A | NA | 70 | 25813/F1 | Yes | 200 | 200 | Yes | 0 | 0 | 0 | 0% | 134 | 91 | 91 | 105% | In side wireing vary poor , | Others | Re-Survey 18 April 2026 | No | Yes | Good | 0.55 | Yes | Yes | Yes | Yes | Good | Good
P2-26 |  | 25.3654 | 51.22 | 12775995 | Yes |  | 8 |  | Bad | 200 | 200 |  |  |  |  | 70 | 25813/F2 |  |  |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% |  |  | No Complete Reports |  | Yes |  | 0 |  |  | Good |  | Good
P2-16 |  | 25.613 | 51.3626 | 1277100 | No | Higher than asphalt level | 8 | 3 | Balanced | 200 | 200 | Yes | 416 | N/A | N/A | 70 | 25812/F3 | Yes | 200 | 250 | Yes | 105 | 116 | 105 | 109% | 66 | 69 | 54 | 63% | Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Need to backfield & change door lock. Also kharamaa meter cabinet need to maintence main cable and door. Re-Suvey 13 April 2026 | No | Yes | Average | 0.63 | Yes | Yes | Very Poor | No | Good | Good
P2-14 | 13159550 | 25.6048 | 51.3558 | 1277119 | No | Higher than asphalt level | 8 | 9 | Normal | 200 | 200 | Yes | 416 | N/A | N/A | 70 | 25811/F1 | Yes | 200 | 250 | Yes | 79 | 96 | 44 | 73% | 52 | 63 | 50 | 55% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Need to clean outside area.Also earthing pit invisible. Kharamaa meter cabinet door damage. Re-Survey 13 April 2026 | No | No | N/A | N/A | Yes | Yes | Good | Yes | Good | Good
P2-15 | 13159549 | 25.6085 | 51.3598 | 1277108 | Yes | Higher than asphalt level | 8 | 6 | Normal | 200 | 200 | Yes | 416 | Yes | MOi-SSD | 70 | 25811/F2 | Yes | 200 | 200 | Yes | 0 | 0 | 0 | 0% | 72 | 50 | 85 | 69% | Corroded/Rusted, Fadded paint or tagging, Foundation backfilled, Others | Found pole foundation burried/ backfilled, Found water accumulation/ stagnant water in the surrounding, Others | Lode not blanced, Re-Survey 13 April 2026 | No | Yes | Average | 0.73 | Yes | Yes | Good | Yes | Good | Average
P2-13 | 13159551 | 25.6027 | 51.3526 | 1277109 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 200 | Yes | 421 | N/A | N/A | 70 | 25810/F2 | Yes | 200 | 250 | Yes | 28 | 136 | 127 | 97% | 67 | 91 | 86 | 81% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition ok, Re-Suvey 13 April 2026 | No | Yes | Good | 0.75 | Yes | Yes | Good | Yes | Good | Average
P2-12 |  | 25.3551 | 51.213 | 1277105 | Yes | Higher than asphalt level | 8 | 3 | Balanced | 200 | 200 | Yes | 423 | N/A | N/A | 70 | 25810/F1 | Yes | 200 | 250 | Yes | 112 | 100 | 135 | 116% | 73 | 78 | 80 | 77% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification | Over all condition is ok, Re-Suvey 14 April 2026 | No | Yes | Good | 0.56 | Yes | Yes | Average | Yes | Good | Average
P1-23 | 13159553 | 25.5904 | 51.3503 | 1274738 | No | Higher than asphalt level | 8 | 6 | Bad | 200 | 200 | Yes | 416 | N/A | N/A | 70 | 25809/F2 | Yes | 200 | 250 | Yes | 77 | 115 | 92 | 95% | 104 | 114 | 92 | 103% | Foundation backfilled, Others | Found damage foundation, Others | Very poor wiring inside, Re-Survey 14 April 2026 | No | Yes | Average | 0.55 | Yes | No | Poor | Yes | Very Poor | Poor
P1-22 | 13160116 | 25.585 | 51.3499 | 1274755 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 200 | Yes | 424 | N/A | N/A | 70 | 25809/F1 | Yes | 200 | 250 | Yes | 70 | 76 | 121 | 89% | 106 | 93 | 99 | 99% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition is ok | No | Yes | Good | 0.77 | Yes | Yes | Average | Yes | Good | Average
P3-1 | 13160092 | 25.4606 | 51.3409 | 1273301 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 423 | N/A | N/A | 70 | 25798/F1 | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 79 | 81 | 83 | 81% | Corroded/Rusted, Fadded paint or tagging | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification | Over all condition is bed, Re-Survey 16 April 2026 | No | Yes | Good | 0.53 | Yes | Yes | Good | Yes | Good | Good
P3-2 | 13160091 | 25.4671 | 51.3414 | 1273300 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 416 | N/A | No | 70 | 25798/F2 | Yes | 200 | 250 | Yes | 87 | 92 | 66 | 82% | 94 | 90 | 82 | 89% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | feeder pilar door damage.Also blower window some broken. Need to maintence. Re-Suvey 16 April 2026 | No | Yes | Good | 0.66 | Yes | Yes | Poor | Yes | Poor | Average
P1-7 | 13160094 | 25.4483 | 51.3394 | 1274779 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 416 | N/A | NA | 70 | 25797/F1 | Yes | 200 | 200 | Yes | 113 | 136 | 157 | 135% | 94 | 97 | 103 | 98% | Others | Others | All good I | No | Yes | Average | 0.84 | Yes | Yes | Good | Yes | Good | Good
P1-6 |  | 25.441 | 51.3378 | 1274780 | No | Higher than asphalt level | 8 | 3 | Normal | 200 | 100 | Yes | 424 | N/A | N/A | 70 | 25796/F3 | Yes | 200 | 250 | Yes | 99 | 101 | 84 | 95% | 84 | 66 | 56 | 68% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Others | Back filling from Road side. Single Barker holding is borkan, Re-Suvey 16 April 2026 | No | Yes | Good | 1.3 | Yes | Yes | Good | Yes | Good | Average
P1-5 | 13158973 | 25.4357 | 51.3366 | 1274782 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 424 | N/A | N/A | 70 | 25796/F1 | Yes | 200 | 250 | Yes | 38 | 82 | 97 | 73% | 116 | 115 | 89 | 107% | Corroded/Rusted, Foundation backfilled | Found corroded bolts, nuts, junction/ distribution box & terminal | Back filling from Road side. Over all condition is ok , Re-Survey 16 Aoril 2026 | No | Yes | Good | 0.68 | Yes | Yes | Good | Yes | Good | Average
P1-4 | 13160097 | 25.4286 | 51.3351 | 1274781 | No | Higher than asphalt level | 8 | 12 | Normal | 200 | 100 | Yes | 423 | N/A | No | 70 | 25823/F2 | Yes | 200 | 200 | Yes | 96 | 33 | 86 | 72% | 64 | 61 | 54 | 60% |  |  |  | No | Yes | Good | 1.05 | Yes | Yes | Good | Yes | Good | Good
P1-3 | 13160098 | 25.4235 | 51.3344 | 1274784 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 430 | N/A | N/A | 70 | 25823/F1 | Yes | 200 | 200 | Yes | 150 | 115 | 75 | 113% | 117 | 152 | 154 | 141% | Corroded/Rusted, Fadded paint or tagging, Foundation backfilled | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification | Over all condition is ok, Re-Survey 17 April 2026 | No | Yes | Good | 0.78 | Yes | Yes | Good | Yes | Good | Average
P1-2 |  | 25.4044 | 51.3378 | No Number | No | Higher than asphalt level | 8 | 9 | Normal | 200 | 100 | No | no | N/A | N/A | 70 | 25794/F2 | Yes | 200 | 200 | Yes | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | power taker from FP p1-3 by HM circuit 4 no meter no SC door - no timer - no photocell - kahramaa cable insulation damage, Re-Survey 19 April 2026 | No | Yes | Good | 0 | No | No | No | No | N/A | Very Poor
P1-1 | 13160100 | 25.4103 | 51.3336 | No Number | No | Higher than asphalt level | 8 | 3 | Normal | 200 | 100 | No | 416 | N/A | N A | 70 | 25794/F1 | Yes | 200 | 200 | Yes | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | Others | Others | On photocell income cable damag mine baker damag No meter and take it's power from FP p-11 by only one phase, Re-Survey 19 April 2026 | No | No | Very Poor | 0 | Yes | Yes | Yes | Yes | Average | Average
P2-11 | 13160101 | 25.4033 | 51.3331 | 1277110 | No | Higher than asphalt level | 8 | 3 | Normal | 200 | 100 | Yes | 416 | N/A | No | 70 | 25793/F2 | Yes | 200 | 250 | Yes | 61 | 66 | 24 | 50% | 102 | 66 | 49 | 72% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Some cable have open.Need to cable check & inside wireing maintenance. Re-Survey 17 April 2026 | No | Yes | Good | 0.77 | Yes | Yes | Average | Yes | Average | Average
P2-10 | 13160102 | 25.398 | 51.332 | 1277111 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 416 | N/A | No | 70 | 25793/F1 | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 61 | 64 | 68 | 64% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Need to backfield , Re-survey 17 April 2026 | No | Yes | Average | 0.93 | Yes | Yes | Good | Yes | Good | Good
P2-TU-1 |  | 25.3915 | 51.3294 | 1290743 | No | Equal | 8 | 18 | Normal | 200 | 100 | Yes | 417 | N/A | No | 70 | 25792/F5 | Yes | 200 | 200 | Yes | 32 | 3 | 24 | 19% | 14 | 3 | 12 | 10% |  |  | Re-Survey 14 April 2026 | No | Yes | Good | 0.1 | Yes | Yes | Good | Yes | Good | Good
P2-9 |  | 25.3914 | 51.3294 | 1277098 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 409 | N/A | No | 70 | 25792/F2 | Yes | 200 | 250 | Yes | 104 | 83 | 79 | 89% | 60 | 54 | 38 | 51% |  |  | Re-Survey 17 April 2026 | No | Yes | Average | 0.76 | Yes | Yes | Good | Yes | Good | Good
P2-5 | 13160111 | 25.3823 | 51.3224 | 1277121 | Yes | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 419 | N/A | N/A | 70 | 25791/F1 | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 93 | 97 | 104 | 98% | Corroded/Rusted, Fadded paint or tagging | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification, Others | Over all condition is ok, Re-Survey 19 April 2026 | No | Yes | Good | 0.62 | Yes | Yes | Yes | Yes | Good | Average
P2-4 | 13160112 | 25.3761 | 51.3217 | 1277112 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 430 | N/A | N/A | 70 | 25791/F2 | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 90 | 87 | 87 | 88% | Corroded/Rusted, Fadded paint or tagging, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification, Others | All door hinges are broken and Photocells hanging in side panel, Re-Survey 18 April 2026 | No | Yes | Good | 0.86 | Yes | Yes | Yes | Yes | Very Poor | Average
P2-3 | 13160113 | 25.3692 | 51.3219 | 1277120 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 416 | N/A | No | 70 | 25790/F1 | Yes | 200 | 250 | Yes | 76 | 121 | 58 | 85% | 96 | 96 | 93 | 95% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Need to backfield.Also some breaker have off position. Bcz makeing load balance. Re-Survey 18 April 2026 | No | Yes | Good | 0.71 | Yes | Yes | Yes | Yes | Good | Good
P2-2 | 13160114 | 25.362 | 51.322 | 1277113 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 422 | N/A | N/A | 70 | 25789/F2 | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 97 | 84 | 69 | 83% | Corroded/Rusted, Fadded paint or tagging, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Found expossed cable, Others | Around the Feeder pillar back filling not good and also cables are exposed, Re-Survey 19 April 2026 | No | Yes | Good | 1.38 | Yes | Yes | Yes | Yes | Good | Average
P2-1 | 13160115 | 25.3569 | 51.322 | 1277106 | No | Higher than asphalt level | 8 | 6 | Normal | 200 | 100 | Yes | 416 | N/A | NA | 70 | 25789/F1 | Yes | 200 | 200 | Yes | 0 | 0 | 0 | 0% | 123 | 83 | 98 | 101% | Corroded/Rusted, Panel location in low level area, Others | Found faded paint and tagging identification, Panel has been newly replaced due to accidental damage, Others | Foundation back fill front fill dangar, Re-Survey 18 April 2026 | No | Yes | Good | 1.11 | Yes | Yes | Yes | Yes | Good | Good
55A |  | 25.3511 | 51.3233 | 1288068 | Yes | Higher than asphalt level | 8 | 10 | Normal | 200 | 100 | Yes | 425 | N/A | N/A | 70 | 29306/F2 | Yes | 200 | 250 | No | 39 | 35 | 34 | 36% | 27 | 25 | 34 | 29% | Corroded/Rusted, Foundation backfilled | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition is ok , Re-Survey 18 April 2026 | No | Yes | Good | 2.27 | Yes | Yes | Yes | Yes | Good | Good
55 |  | 25.3512 | 51.3233 | 1288069 | Yes | Higher than asphalt level | 8 | 10 | Normal | 200 | 100 | Yes | 417 | N/A | N/A | 70 | 29306/F1 | Yes | 200 | 250 | No | 22 | 52 | 88 | 54% | 75 | 82 | 66 | 74% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition is ok, Re-Survey 18 April 2026 | No | Yes | Good | 2.35 | Yes | Yes | Yes | Yes | Good | Good
52 |  | 25.3414 | 51.3222 | 1288094 | Yes | Higher than asphalt level | 8 | 4 | Normal | 200 | 100 | Yes | 427 | N/A | N/A | 70 | 29306/F4 | Yes | 200 | 250 | No | 0 | 0 | 0 | 0% | 51 | 50 | 45 | 49% | Corroded/Rusted, Fadded paint or tagging | Found corroded bolts, nuts, junction/ distribution box & terminal, Found expossed cable | Over all condition is ok , Re-Survey 18 April 2026 | No | Yes | Good | 1.95 | Yes | Yes | Yes | Yes | Good | Good
P3-9 | 13159523 | 25.6347 | 51.3861 | 1273257 | Yes | Higher than asphalt level | 8 | 6 | Bad | 200 | 100 | Yes | 431 | N/A | N/A | 70 | 25816/F1 | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 56 | 90 | 60 | 69% | Others | Others | Re-Survey 12 April 2026 | No | Yes | Average | 0.99 | Yes | Yes | Poor | Yes | Good | Poor
P3-8 |  | 25.6297 | 51.3808 | 1273258 | Yes | Higher than asphalt level | 8 | 6 | Bad | 200 | 200 | Yes | 416 | N/A | N/A | 70 | 25815/F2 | Yes | 200 | 200 | Yes | 106 | 107 | 129 | 114% | 73 | 60 | 70 | 68% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification, Found pole foundation burried/ backfilled, Found damage foundation | Kharrama meter panel foundshan poor , Re-Survey 13 April 2026 | No | Yes | Average | 0.99 | Yes | Yes | Poor | Yes | Good | Average
P2-23 | 13159537 | 25.6249 | 51.3756 | 1277117 | No | Lower than asphalt level | 8 | 6 | Balanced | 200 | 200 | Yes | 427 | N/A | N/A | 70 | 25815/F1 | Yes | 200 | 250 | Yes | 102 | 47 | 72 | 74% | 92 | 92 | 85 | 89% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition ok, Re-Survey 13 April 2026 | No | Yes | Good | 1.12 | Yes | Yes | Average | Yes | Average | Average
P2-19 | 13159539 | 25.6201 | 51.3705 | 1275998 | No | Higher than asphalt level | 8 |  | Balanced | 200 | 200 | Yes | 416 | N/A | No | 70 | 25813/F2 | Yes | 200 | 200 | Yes | 33 | 67 | 56 | 52% | 34 | 72 | 70 | 59% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Need to maintence door lock & inside wireing.Also blower window maintenance, Re-Survey 16 April 2026 | No | Yes | Good | 1.13 | Yes | No | Poor | No | Poor | Average
P3-12 | 13159527 | 25.6431 | 51.3996 | 1284860 | No | Equal | 8 |  | Good | 200 | 150 | Yes | 416 | N/A | N/A | 70 | 25818/F3 | Yes | 200 | 250 | Yes | 119 | 138 | 113 | 123% | 78 | 97 | 85 | 87% |  |  | Re-Survey 12 April 2026 | No | Yes | Good | 0.48 | Yes | Yes | Good | Yes | Good | Poor
P3-17 | 13159532 | 25.6653 | 51.4218 | 1284859 | No | Higher than asphalt level | 6 | 6 | Good | 200 | 100 | Yes | 420 | N/A | N/A | 70 | 25820/F1 | Yes | 200 | 200 | Yes | 117 | 85 | 120 | 107% | 73 | 66 | 87 | 75% | Fadded paint or tagging, Foundation backfilled | Found pole foundation burried/ backfilled | Re-Survey 12 April 2026 | No | Yes | Poor | 1.11 | Yes | Yes | Poor | No | Poor | Average
P3-16 |  | 25.6597 | 51.4168 | 1284864 | Yes | Higher than asphalt level | 6 | 6 | Good | 200 |  | Yes | 426 | N/A | N/A | 70 | 25819/F2 | Yes | 200 | 200 | Yes | 89 | 89 | 71 | 83% | 49 | 49 | 38 | 46% | Others | Others | Re-Survey 12 April 2026 | No | Yes | Good | 1.87 | Yes | Yes | Good | Yes | Good | Good
P3-15 | 13159530 | 25.6554 | 51.413 | 1284863 | Yes | Higher than asphalt level | 6 | 6 | Good | 200 | 100 | Yes | 426 | N/A | NA | 70 | 25819/F1 | Yes | 200 | 200 | Yes | 9 | 92 | 83 | 61% | 59 | 59 | 42 | 53% | Fadded paint or tagging, Foundation backfilled, Panel location in low level area, Panel damaged and replaced, Others | Found pole foundation burried/ backfilled, Found expossed cable, Found water accumulation/ stagnant water in the surrounding, Panel has been newly replaced due to aging and deterioration, Panel has been newly replaced due to accidental damage | New changed that panel, Re-Survey 12 April 2026 | No | Yes | Poor | 2.46 | Yes | Yes | Average | Yes | Poor | Poor
P3-14 | 13159529 | 25.6497 | 51.408 | 1284861 | Yes | Higher than asphalt level | 8 | 6 | Good | 200 | 100 | Yes | 416 | N/A | N/A | 70 | 25818/F2 | Yes | 200 | 250 | Yes | 104 | 91 | 90 | 95% | 54 | 59 | 58 | 57% | Corroded/Rusted, Foundation backfilled, Panel damaged and replaced | Found corroded bolts, nuts, junction/ distribution box & terminal, Found faded paint and tagging identification, Found pole foundation burried/ backfilled, Panel has been newly replaced due to aging and deterioration | Need to change feeder pilar, Re-Survey 12 April 2026 | No | Yes | Average | 0.8 | Yes | Yes | Good | Yes | Good | Average
P3-13 |  | 25.645 | 51.4029 | 1284862 | Yes | Higher than asphalt level | 8 | 3 | Good | 200 |  | Yes | 416 | N/A | NA | 70 | 25818/F1 | Yes | 200 | 250 | Yes | 119 | 119 | 91 | 110% | 74 | 75 | 48 | 66% | Corroded/Rusted, Fadded paint or tagging, Foundation backfilled, Panel location in low level area, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Found water accumulation/ stagnant water in the surrounding, Panel has been newly replaced due to accidental damage | Re-Survey 12 April 2026 | No | Yes | Average | 1.04 | Yes | Yes | Average | Yes | Average | Average
P3-18 | 13159533 | 25.6699 | 51.4258 | 1284858 | Yes | Higher than asphalt level | 8 | 10 | Good | 200 | 100 | Yes | 424 | N/A | N/A | 70 | 25820/F2 | Yes | 200 | 250 | Yes | 42 | 57 | 48 | 49% | 54 | 61 | 44 | 53% | Others | Others | Re-Survey 12 April 2026 | No | Yes | Poor | 3.94 | Yes | Yes | Good | Yes | Good | Poor
P2-6 | 13160109 | 25.3882 | 51.3261 | 1277097 | Yes | Higher than asphalt level | 8 | 9 | Bad | 200 | 100 | Yes | 422 | N/A | N/A | 70 | 25791/F1 | Yes | 200 | 250 | Yes | 118 | 106 | 112 | 112% | 75 | 67 | 72 | 71% | Corroded/Rusted, Fadded paint or tagging | Found corroded bolts, nuts, junction/ distribution box & terminal | 2 door hinges are broken and breaker strip not fit, Re-Survey 17 April 2026 | No | Yes | Good | 0.64 | Yes | No | Average | Yes | Very Poor | Average
P2-7 |  | 25.3887 | 51.3277 | 1277095 | No | Higher than asphalt level | 8 | 6 | Good | 200 | 100 | Yes | 416 | N/A | N/A | 70 | 25792/F6 | Yes | 200 | 200 | Yes | 11 | 19 | 32 | 20% | 9 | 12 | 11 | 10% | Corroded/Rusted, Foundation backfilled | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Need to backfield, Re-Survey 18 April 2026 | No | Yes | Good | 0.46 | Yes | Yes | Yes | Yes | Good | Good
P2-TU-2 | 13160105 | 25.3913 | 51.3279 | 1290741 | Yes | Higher than asphalt level | 6 | 10 | Good | 200 | 200 | Yes | 422 | N/A | N/A | 70 | 25792/F6 | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 13 | 14 | 11 | 13% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal, Found expossed cable | Over all condition is ok Re-Survey 17 April 2026 | No | Yes | Good | 0.65 | Yes | Yes | Good | Yes | Good | Good
P2-8 |  | 25.3913 | 51.3281 | 1276380 | Yes | Higher than asphalt level | 6 | 10 | Normal | 200 | 100 | Yes | 415 | N/A | N/A | 70 | 25792/F2 | Yes | 200 | 250 | Yes | 106 | 126 | 148 | 127% | 113 | 98 | 113 | 108% | Corroded/Rusted | Found corroded bolts, nuts, junction/ distribution box & terminal | Over all condition is ok, BG71154 Re-Survey 17 April 2026 | Yes | Yes | Good | 0.66 | Yes | Yes | Good | Yes | Good | Good
P3-5A |  | 25.2827 | 51.2048 | 1273305 | Yes |  | 8 |  | Good | 200 | 100 |  |  |  |  | 70 | 25799/F4 |  |  |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% |  |  | No Inrush, Incomplete Reports |  | Yes |  | 0 | 0 | 0 | Good | 0 | Good | 0
P3-5B |  | 25.2855 | 51.2045 | 1273306 | Yes |  | 8 |  | Good | 200 | 100 |  |  |  |  | 70 | 22799/F3 |  |  |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% |  |  | No Inrush, Incomplete Reports |  | Yes |  | 0 | 0 | 0 | Good | 0 | Good | 0
P3-5D |  | 25.2913 | 51.2029 | 1283462 | No |  | 8 |  | Normal | 200 | 100 |  |  |  |  | 70 | 25800/F5 |  |  |  |  | 85 | 69 | 18 | 57% | 85 | 69 | 18 | 57% |  |  |  |  | Don’t have |  | 0.34 | 0 | 0 | Poor | 0 | Poor | 0
P2-20 |  | 25.3648 | 51.2153 | 1275997 | Yes |  | 8 |  | Normal | 200 | 100 |  |  |  |  | 70 | 25813/F3 |  |  |  |  | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% |  |  | No Inrush, Incomplete Reports |  | Yes |  | 0 | 0 | 0 | Poor | 0 | Poor | 0
P3-20 | 13159535 | 25.6793 | 51.4342 | 1284856 | Yes | Lower than asphalt level | 8 | 4 | Normal | 200 |  | Yes | 422 | N/A | N/A | 70 | 25821/F2 | Yes | 200 | 200 | Yes | 69 | 99 | 67 | 78% | 47 | 60 | 43 | 50% |  |  |  | No | Yes | Average | 4.37 | Yes | Yes | Good | Yes | Average | Good
P3-21 | 13159536 | 25.6835 | 51.438 | 1273254 | Yes | Equal | 8 | 4 | Normal | 200 |  | Yes | 422 | N/A | N/A | 70 | 25822/F1 | Yes | 200 | 200 | No | 49 | 68 | 83 | 66% | 66 | 66 | 57 | 63% | Fadded paint or tagging, Foundation backfilled, Panel damaged and replaced, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found expossed cable, Panel has been newly replaced due to aging and deterioration, Panel has been newly replaced due to accidental damage, Others | All damag | No | Yes | Average | 0.98 | Yes | Yes | Average | Yes | Average | Average
P3-19 | 13159534 | 25.6751 | 51.43 | 1284857 | Yes | Equal | 8 | 4 | Normal | 200 |  | Yes | 425 | N/A | N/A | 70 | 25821/F1 | Yes | 200 | 200 | Yes | 62 | 79 | 87 | 76% | 55 | 57 | 60 | 57% |  |  | Back filling not good All cables exposed | No | Yes | Poor | 4.57 | Yes | Yes | Good | Yes | Good | Good
P3-10 | 13159524 | 25.6395 | 51.3917 | 1273256 | Yes | Higher than asphalt level | 8 | 6 |  | 200 |  | Yes | 426 | N/A | N/A | 70 |  | Yes | 200 | 250 | Yes | 62 | 35 | 93 | 63% | 64 | 50 | 49 | 54% | Others | Others | N/A | No | No | N/A | 0.37 | Yes | Yes | Poor | Yes | Good | Poor
P3-11 | 13159525 | 25.6405 | 51.3937 | 1273255 | No | Higher than asphalt level | 8 | 6 |  | 200 |  | Yes | 416 | N/A | N/A | 70 |  | Yes | 200 | 200 | Yes | 46 | 90 | 66 | 67% | 26 | 50 | 57 | 44% | Fadded paint or tagging, Foundation backfilled | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled | Kharamaa meter cabinet need to clean & maintenance. Also earthing pit invisible. | No | No | N/A | 0.9 | Yes | Yes | Average | Yes | Good | Average
P2-26 |  | 25.6151 | 51.3667 | 1275995 | No | Higher than asphalt level | 8 | 10 |  | 200 |  | Yes | 430 | N/A | N/A | 70 |  | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 22 | 26 | 17 | 21% | Fadded paint or tagging, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Others | Panel door damaged | No | Yes | Good | 1.45 | No | No | Very Poor | Yes | Very Poor | Average
P2-27 |  | 25.6203 | 51.3698 | 1276379 | No | Higher than asphalt level | 8 | 10 |  | 200 |  | Yes | 425 | Yes | Irrigation | 70 |  | Yes | 200 | 250 | Yes | 11 | 19 | 32 | 20% | 9 | 12 | 11 | 10% | Corroded/Rusted, Fadded paint or tagging | Found corroded bolts, nuts, junction/ distribution box & terminal, Found unused cable inside the feeder pillar panel | Over all condition is ok | No | Yes | Good | 1.41 | Yes | Yes | Good | Yes | Good | Average
P1-13 | 13151082 | 25.5276 | 51.3458 | 1277096 | No | Higher than asphalt level | 8 | 3 |  | 200 |  | Yes | 416 | N/A | No | 70 |  | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 43 | 44 | 58 | 48% | Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | All good | No | Yes | Good | 1.22 | Yes | Yes | Average | Yes | Average | Average
P2-21 |  | 25.4033 | 51.438 |  | No | Higher than asphalt level | 8 | 3 |  | 200 |  | Yes | 416 | N/A | NA | 70 | 25793/F2 | Yes | 200 | 200 | No | 0 | 0 | 0 | 0% | 108 | 97 | 87 | 97% | Fadded paint or tagging, Foundation backfilled, Panel damaged and replaced, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found expossed cable, Panel has been newly replaced due to aging and deterioration, Panel has been newly replaced due to accidental damage, Others | All damag | No | Yes | Average | 0.98 | Yes | Yes | Average | Yes | Average | Average
P1-8 | 13160093 | 25.4534 | 51.3404 | 1274766 | No | Higher than asphalt level | 8 | 10 |  | 200 |  | Yes | 416 | N/A | No | 70 |  | Yes | 200 | 250 | Yes | 67 | 95 | 58 | 74% | 63 | 65 | 63 | 64% | Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Need to backfield | No | Yes | Good | 1.08 | Yes | Yes | Average | Yes | Average | Average
P2-TU-4 | 13160109 | 25.3881 | 51.326 | 1290740 | Yes | Higher than asphalt level | 8 | 10 |  | 200 |  | Yes | 423 | N/A | N/A | 70 |  | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 10 | 11 | 10 | 10% | Fadded paint or tagging | Found faded paint and tagging identification | Over all condition is ok | No | Yes | Good | 0.75 | Yes | Yes | Good | Yes | Good | Good
P2-TU-3 | 13160108 | 25.3886 | 51.3276 | 1290842 | No | Higher than asphalt level | 8 | 10 |  | 200 |  | Yes | 416 | N/A | NA | 70 | S S 25792/ F4 | Yes | 200 | 200 | Yes | 22 | 30 | 31 | 28% | 10 | 12 | 14 | 12% | Others | Others | All ok | No | Yes | Average | 0.48 | Yes | Yes | Yes | Yes | Good | Good
P2-17 | 13159543 | 25.6176 | 51.3643 | 1277099 | No | Higher than asphalt level | 8 | 2 |  | 200 |  | Yes | 416 | N/A | No | 70 | S.S/25812/F2 | Yes | 200 | 250 | Yes | 0 | 0 | 0 | 0% | 43 | 32 | 30 | 35% | Corroded/Rusted, Foundation backfilled, Others | Found corroded bolts, nuts, junction/ distribution box & terminal, Found pole foundation burried/ backfilled, Others | Need to backfield.Also kharamaa meter cabinet door damage.& main cable insulation damage. | No | Yes | Good | 1.39 | Yes | Yes | Yes | Yes | Very Poor | Average
54 |  | 25.3453 | 51.3221 | 1288096 | No | Higher than asphalt level | 8 | 6 |  | 200 |  | Yes | 415 | N/A | N/A | 70 | S S - 19306-F1 | Yes | 200 | 200 | Yes | 0 | 0 | 0 | 0% | 97 | 72 | 74 | 81% | Others | Others | All ok | No | No | N/A | 0 | No | Yes | Yes | Yes | Good | Good